Ref. no: CRTC/CEE/ G20220696/S- 116

SUB-SOIL INVESTIGATION REPORT FOR PROPOSED CONSTRUCTION OF 05 STORIED SAJIDA MENTAL HEALTH RESIDENTIAL FACILITY(SMHRE) BUILDING AT CHUNARUGHAT, HOBIGONJ DAG # SA-599,652,653,654,655,661, BS-996,997,998,999,1003,1030, KHA # SA-1357,1359,1531,1694, BS/DP-864, MOUJA- NAROPATI.

CLIENT CHIEF EXECUTIVE OFFICER SAJIDA FOUNDATION

CONDUCTED BY CENTER FOR RESEARCH TESTING & CONSULTANCY DEPARTMENT OF CIVIL & ENVIRONMENTAL ENGINEERING SHAHJALAL UNIVERSITY OF SCIENCE & TECHNOLOGY, SYLHET

SAMPLE COLLECTED BY

THE SOIL ENGINEERS & CONSULTANT 6 NAHAR SHOPPING COMPLEX (GL FL) SUBHANIGHAT POINT, SYLHET. MOBILE: 01711-737479

##### Introduction

A reasonably accurate conception about the sub-soil parameters of any project site is an essential prerequisite for proper planning and designing the foundation of the structure so that the same after its construction would remain safe and serviceable. A detailed study on the sub-surface elements in this regard would necessary to select proper type of foundation.

Objectives

The purpose of sub-soil investigation program is to obtain the following information

- To classify the formation of soil layers

- To estimate the safe bearing capacities of the foundation at different soil layers

- To suggest the safe and appropriate type of foundations.

Scope of work

Centre for research, testing and consultancy (CRTC), Department of Civil and Environmental Engineering, Shahjalal University of Science & Technology (SUST), Sylhet; execute only the laboratory tests and other computational works with the supplied disturbed and/or undisturbed samples to determine the geotechnical properties of the soil.

Table – 1: Items of the supplied samples

| No | Name | Bore hole no | Depth | Quantities |
| --- | --- | --- | --- | --- |
| 01 | Disturbed sample | 01 | 0-50 ft | 10 |
| 02 | Disturbed sample | 02 | 0-50 ft | 10 |
| 03 | Disturbed sample | 03 | 0-50 ft | 10 |
| 04 | Disturbed sample | 04 | 0-50 ft | 10 |
| 05 | Disturbed sample | 05 | 0-50 ft | 10 |
| - | - | - | - | - |
| - | - | - | - | - |
| - | - | - | - | - |
| - | - | - | - | - |
| - | - | - | - | - |
| - | - | - | - | - |
| - | - | - | - | - |
| - | - | - | - | - |
| - | - | - | - | - |

# Laboratory Classifications

The disturbed soil samples, supplied by the client were thoroughly examined and classified roughly (color and type) and noted in accordance with bore hole (BH) and depth (Please see enclosed Tables).

Laboratory Works & Analysis

In addition to visual examination of the sample, Bearing Capacity of soil samples including skin friction & end bearing were calculated.

Bearing capacity for shallow foundation

The N value gives useful information with regards to consistency of cohesive soil and relative density of cohesion less soil. These relationships are given in the following Tables for cohesive and cohesion less soil, respectively.

# Table 2: Relation of N-value with the Consistency and the Unconfined Compressive Strength of Cohesive Soils (after Bowles 1997)

| N-values | Consistency | Unconfined Compressive Strength (qu) |  |
| --- | --- | --- | --- |
|  |  | tsf | kPa |
| 0-2 | Very soft | 0 to 0.25 | 0 to 25 |
| 3-5 | Soft | 0.25 to 0.50 | 25 to 50 |
| 6-9 | Medium | 0.50 to 1 | 50 to 100 |
| 10-16 | Stiff | 1 to 2 | 100 to 200 |
| 17-30 | Very stiff | 2 to 4 | 200 to 400 |
| >30 | Hard | >4 | >400 |

# Table 3: N and  Relation to Relative Density for Fine Sand (after Bowles 1997)

| N values | Compactness | Relative Density, Dr % | (degree) | Unit Weight (pcf) |
| --- | --- | --- | --- | --- |
| 1 – 2 | Very Loose | 0 – 15 | 26 – 28 | 70 – 100 |
| 3 – 6 | Loose | 15 – 35 | 28 – 30 | 90 – 115 |
| 7 – 15 | Medium | 35 – 65 | 30 – 34 | 110 – 130 |
| 16 – 30 | Dense | 65 – 85 | 33 – 38 | 110 – 140 |
| >30 | Very Dense | >85 | >50 | 130 – 150 |

# Table 4: N and  Relation to Relative Density for Medium Sand (after Bowles 1997)

| N values | Compactness | Relative Density, Dr % | (degree) | Unit Weight (pcf) |
| --- | --- | --- | --- | --- |
| 2 – 3 | Very Loose | 0 – 15 | 27 – 28 | 70 – 100 |
| 4 – 7 | Loose | 15 – 35 | 30 – 32 | 90 – 115 |
| 8 – 20 | Medium | 35 – 65 | 32 – 36 | 110 – 130 |
| 21 – 40 | Dense | 65 – 85 | 36 – 42 | 110 – 140 |

# Table 5: N and  Relation to Relative Density for Coarse Sand (after Bowles 1997)

| N values | Compactness | Relative Density, Dr % | (degree) | Unit Weight (pcf) |
| --- | --- | --- | --- | --- |
| 3 – 6 | Very Loose | 0 – 15 | 28 – 30 | 70 – 100 |
| 5 – 9 | Loose | 15 – 35 | 30 – 34 | 90 – 115 |
| 10 – 25 | Medium | 35 – 65 | 33 – 40 | 110 – 130 |
| 26 – 40 | Dense | 65 – 85 | 40 – 50 | 110 – 140 |
| >40 | Very Dense | >85 | >50 | 130 – 150 |

Bearing capacity for deep foundation

Foundations, preferably piles are considered to transmit heavy load from superstructure to deep and hard strata. As the formation of soil strata consists of cohesive and non-cohesive type, the evaluation criteria for the determination of skin friction and the end bearing capacities of piles also vary. Details of the evaluation are provided in the following sub-headings.

Table 6: Formula Used to Determine Bearing Capacity of Soil

| Shallow Foundation |  |
| --- | --- |
| For Cohesive Soil |  |
| qa=qu+γD3 qa=qu(Common Practice) | Where, qa = Allowable bearing capacity, qu = Unconfined Compressive Strength, γ = Unit Weight of soil, D = Depth of footing |
| For Cohesion less Soil |  |
| qult=30N; qa=qultFS | qult = Ultimate bearing capacity in kPa, N = SPT Number, FS = Factor of Safety |
| Source: Bowles, J. E., "Physical and Geotechnical Properties of Soils", 2nd Edition |  |
| Deep Foundation |  |
| For Cohesive Soil |  |
| fsu=αCu ; qpu=NcCu | = Adhesion factor, fsu= Ultimate skin friction, Cu= Undrained Shear Strength, qpu= Ultimate end bearing of pile, Nc= Bearing capacity factor for deep foundation = 9 |
| For Cohesion less Soil |  |
| fsu=N50 tsf; qpu=4N tsf | fsu= Ultimate skin friction, qpu= Ultimate end bearing of pile, N = SPT Number |
| Source: Rajapakse RA (2008), “Geotechnical Engineering Calculations and Rules of Thumb” |  |

Based on the above formula, the important parameters for foundation design have been determined and are given in Tables 7-11.

Table 7: The allowable bearing capacity for shallow foundation in Tsf (FS = 2.5)

| Bore Hole No. | Depth | Design N | Clay |  |  |  |  |  | Sand |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Continuous |  |  | Square (Isolated) |  |  |  |
|  | (ft) | - | D/B=0.25 | D/B=0.5 | D/B=1 | D/B=0.25 | D/B=0.5 | D/B=1 |  |
| BH01 | 2.5-5.0 | 14 | 1.647 | 1.732 | 1.889 | 1.945 | 2.102 | 2.286 | 1.775 |
|  | 5.0-10 | 19 | 2.216 | 2.331 | 2.541 | 2.617 | 2.827 | 3.076 | 2.388 |
| BH02 | 2.5-5.0 | 8 | 0.974 | 1.025 | 1.117 | 1.151 | 1.243 | 1.352 | 1.050 |
|  | 5.0-10 | 15 | 1.708 | 1.796 | 1.958 | 2.017 | 2.179 | 2.371 | 1.841 |
| BH03 | 2.5-5.0 | 2 | 0.278 | 0.293 | 0.319 | 0.329 | 0.355 | 0.386 | 0.300 |
|  | 5.0-10 | 4 | 0.432 | 0.454 | 0.495 | 0.510 | 0.551 | 0.600 | 0.466 |
| BH04 | 2.5-5.0 | 10 | 1.206 | 1.269 | 1.383 | 1.425 | 1.539 | 1.674 | 1.300 |
|  | 5.0-10 | 16 | 1.848 | 1.944 | 2.119 | 2.183 | 2.358 | 2.565 | 1.991 |
| BH05 | 2.5-5.0 | 5 | 0.603 | 0.634 | 0.692 | 0.712 | 0.770 | 0.837 | 0.650 |
|  | 5.0-10 | 10 | 1.148 | 1.207 | 1.316 | 1.356 | 1.465 | 1.593 | 1.237 |
| BH06 | 2.5-5.0 | - | - | - | - | - | - | - | - |
|  | 5.0-10 | - | - | - | - | - | - | - | - |
| BH07 | 2.5-5.0 | - | - | - | - | - | - | - | - |
|  | 5.0-10 | - | - | - | - | - | - | - | - |
| BH08 | 2.5-5.0 | - | - | - | - | - | - | - | - |
|  | 5.0-10 | - | - | - | - | - | - | - | - |
| BH09 | 2.5-5.0 | - | - | - | - | - | - | - | - |
|  | 5.0-10 | - | - | - | - | - | - | - | - |
| BH10 | 2.5-5.0 | - | - | - | - | - | - | - | - |
|  | 5.0-10 | - | - | - | - | - | - | - | - |

Table 8: The allowable skin friction for Precast driven piles in Tsf (FS = 2.5)

| Depth | Bore Hole |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ft | BH01 | BH02 | BH03 | BH04 | BH05 | BH06 | BH07 | BH08 | BH09 | BH10 |
| 5 | 0.118 | 0.049 | 0.049 | 0.049 | 0.049 | - | - | - | - | - |
| 10 | 0.226 | 0.074 | 0.049 | 0.174 | 0.074 | - | - | - | - | - |
| 15 | 0.136 | 0.136 | 0.074 | 0.240 | 0.196 | - | - | - | - | - |
| 20 | 0.321 | 0.308 | 0.138 | 0.294 | 0.240 | - | - | - | - | - |
| 25 | 0.669 | 0.669 | 0.495 | 0.615 | 0.218 | - | - | - | - | - |
| 30 | 0.669 | 0.669 | 0.669 | 0.589 | 0.375 | - | - | - | - | - |
| 35 | 0.669 | 0.118 | 0.482 | 0.669 | 0.548 | - | - | - | - | - |
| 40 | 0.138 | 0.156 | 0.375 | 0.241 | 0.375 | - | - | - | - | - |
| 45 | 0.208 | 0.669 | 0.669 | 0.669 | 0.669 | - | - | - | - | - |
| 50 | 0.200 | 0.669 | 0.669 | 0.803 | 0.669 | - | - | - | - | - |
| 55 | - | - | - | - | - | - | - | - | - | - |
| 60 | - | - | - | - | - | - | - | - | - | - |
| 65 | - | - | - | - | - | - | - | - | - | - |
| 70 | - | - | - | - | - | - | - | - | - | - |
| 75 | - | - | - | - | - | - | - | - | - | - |
| 80 | - | - | - | - | - | - | - | - | - | - |
| 85 | - | - | - | - | - | - | - | - | - | - |
| 90 | - | - | - | - | - | - | - | - | - | - |
| 95 | - | - | - | - | - | - | - | - | - | - |
| 100 | - | - | - | - | - | - | - | - | - | - |

Table 9: The allowable end bearing for Precast driven piles in Tsf (FS = 2.5)

| Depth | Bore Hole |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ft | BH01 | BH02 | BH03 | BH04 | BH05 | BH06 | BH07 | BH08 | BH09 | BH10 |
| 5 | 1.125 | 0.450 | 0.450 | 0.450 | 0.450 | - | - | - | - | - |
| 10 | 3.600 | 0.675 | 0.450 | 1.800 | 0.675 | - | - | - | - | - |
| 15 | 27.200 | 27.200 | 0.675 | 3.825 | 2.025 | - | - | - | - | - |
| 20 | 5.400 | 5.175 | 1.350 | 4.950 | 3.825 | - | - | - | - | - |
| 25 | 11.250 | 11.250 | 8.325 | 10.350 | 2.250 | - | - | - | - | - |
| 30 | 11.250 | 11.250 | 11.250 | 9.900 | 6.300 | - | - | - | - | - |
| 35 | 11.250 | 1.125 | 8.100 | 11.250 | 9.225 | - | - | - | - | - |
| 40 | 1.350 | 1.575 | 6.300 | 4.050 | 6.300 | - | - | - | - | - |
| 45 | 41.600 | 11.250 | 11.250 | 11.250 | 11.250 | - | - | - | - | - |
| 50 | 40.000 | 11.250 | 11.250 | 13.500 | 11.250 | - | - | - | - | - |
| 55 | - | - | - | - | - | - | - | - | - | - |
| 60 | - | - | - | - | - | - | - | - | - | - |
| 65 | - | - | - | - | - | - | - | - | - | - |
| 70 | - | - | - | - | - | - | - | - | - | - |
| 75 | - | - | - | - | - | - | - | - | - | - |
| 80 | - | - | - | - | - | - | - | - | - | - |
| 85 | - | - | - | - | - | - | - | - | - | - |
| 90 | - | - | - | - | - | - | - | - | - | - |
| 95 | - | - | - | - | - | - | - | - | - | - |
| 100 | - | - | - | - | - | - | - | - | - | - |

Table 10: The allowable skin friction for Bored piles in Tsf (FS = 2.5)

| Depth | Bore Hole |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ft | BH01 | BH02 | BH03 | BH04 | BH05 | BH06 | BH07 | BH08 | BH09 | BH10 |
| 5 | 0.077 | 0.032 | 0.032 | 0.032 | 0.032 | - | - | - | - | - |
| 10 | 0.147 | 0.048 | 0.032 | 0.113 | 0.048 | - | - | - | - | - |
| 15 | 0.088 | 0.088 | 0.048 | 0.156 | 0.127 | - | - | - | - | - |
| 20 | 0.209 | 0.200 | 0.090 | 0.191 | 0.156 | - | - | - | - | - |
| 25 | 0.435 | 0.435 | 0.322 | 0.400 | 0.141 | - | - | - | - | - |
| 30 | 0.435 | 0.435 | 0.435 | 0.383 | 0.243 | - | - | - | - | - |
| 35 | 0.435 | 0.077 | 0.313 | 0.435 | 0.356 | - | - | - | - | - |
| 40 | 0.090 | 0.101 | 0.243 | 0.156 | 0.243 | - | - | - | - | - |
| 45 | 0.135 | 0.435 | 0.435 | 0.435 | 0.435 | - | - | - | - | - |
| 50 | 0.130 | 0.435 | 0.435 | 0.522 | 0.435 | - | - | - | - | - |
| 55 | - | - | - | - | - | - | - | - | - | - |
| 60 | - | - | - | - | - | - | - | - | - | - |
| 65 | - | - | - | - | - | - | - | - | - | - |
| 70 | - | - | - | - | - | - | - | - | - | - |
| 75 | - | - | - | - | - | - | - | - | - | - |
| 80 | - | - | - | - | - | - | - | - | - | - |
| 85 | - | - | - | - | - | - | - | - | - | - |
| 90 | - | - | - | - | - | - | - | - | - | - |
| 95 | - | - | - | - | - | - | - | - | - | - |
| 100 | - | - | - | - | - | - | - | - | - | - |

Table 11: The allowable end bearing for Bored piles in Tsf (FS = 2.5)

| Depth | Bore Hole |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ft | BH01 | BH02 | BH03 | BH04 | BH05 | BH06 | BH07 | BH08 | BH09 | BH10 |
| 5 | 0.506 | 0.203 | 0.203 | 0.203 | 0.203 | - | - | - | - | - |
| 10 | 1.620 | 0.304 | 0.203 | 0.810 | 0.304 | - | - | - | - | - |
| 15 | 12.240 | 12.240 | 0.304 | 1.721 | 0.911 | - | - | - | - | - |
| 20 | 2.430 | 2.329 | 0.608 | 2.228 | 1.721 | - | - | - | - | - |
| 25 | 5.063 | 5.063 | 3.746 | 4.658 | 1.013 | - | - | - | - | - |
| 30 | 5.063 | 5.063 | 5.063 | 4.455 | 2.835 | - | - | - | - | - |
| 35 | 5.063 | 0.506 | 3.645 | 5.063 | 4.151 | - | - | - | - | - |
| 40 | 0.608 | 0.709 | 2.835 | 1.823 | 2.835 | - | - | - | - | - |
| 45 | 18.720 | 5.063 | 5.063 | 5.063 | 5.063 | - | - | - | - | - |
| 50 | 18.000 | 5.063 | 5.063 | 6.075 | 5.063 | - | - | - | - | - |
| 55 | - | - | - | - | - | - | - | - | - | - |
| 60 | - | - | - | - | - | - | - | - | - | - |
| 65 | - | - | - | - | - | - | - | - | - | - |
| 70 | - | - | - | - | - | - | - | - | - | - |
| 75 | - | - | - | - | - | - | - | - | - | - |
| 80 | - | - | - | - | - | - | - | - | - | - |
| 85 | - | - | - | - | - | - | - | - | - | - |
| 90 | - | - | - | - | - | - | - | - | - | - |
| 95 | - | - | - | - | - | - | - | - | - | - |
| 100 | - | - | - | - | - | - | - | - | - | - |

CONCLUSION AND RECOMMENDATION

On the basis of analysis and information provided by the client, following recommendations are suggested for the proposed five-storied Sajida Mental Health Residential Facility building.

Soil profile scenario

Overall soil information of the investigated site is slightly irregular in between the boreholes and little vertical inconsistency exists in the soil formation. The topsoil up to 10 ft is brown/ grey soft clay in all the borehole locations with low bearing capacity. Grey/white fine sand/ stiff clay with moderate bearing capacity has been observed in borehole locations 1, 2 and 4 at 15 ft from existing ground level. Grey hard clay with goo to very good bearing capacity have been found after 15/25 depth from EGL. One/two grey soft/stiff clay layer have been observed in borehole locations 1, 2 and 3 at 35/40 ft depth from EGL. After that fine sand or hard clay with very good bearing capacity have found in all the borehole locations.

Foundation options

In this situation, the foundation should be selected considering the dimension, design load for the proposed building and bearing capacity of the soil. Shallow foundation should not be provided in this case. However, pile foundation (cast in-situ pile) may be selected as the most suitable option in this case. For designing any suitable deep foundation, the necessary data for skin friction and end bearing can be found from the attached tables (8-11) in the report which is provided based on the test values provided.

Safety provisions

From the practical viewpoint, it has been found in many buildings that the structure failed due to soil settlement or judging the soil parameters incorrectly, providing no signs of structural damage. It is safe to consult a foundation (geotechnical) specialist before deciding on the foundation type, size and depth. The earthquake vulnerability of the project area as well as the quality management of the construction work including workmanship should be taken into account for the safe design of a foundation.

Attachments

The layout of the boreholes of the investigated site and the bore-log profiles with SPT values are shown in the Appendix. Client performed no special laboratory test for the proposed site.

Special notes

These suggestions are absolutely tentative and the selection of type, depth and dimensions of foundation would be decided by the Geotechnical Consultant or Design Engineer. It is also to be noted that the above recommendation is restricted only to the existing soil condition, which is up to 50 ft as the client provided.

| Test Assisted By | Report Prepared By | Countersigned By |
| --- | --- | --- |
| A H M Humayun Kabir | Dr. Shriful Islam | # Prof. Dr. H.M.A. Mahzuz |
| Senior Technical Officer Dept. of CEE, SUST-3114 | Associate Professor Dept. of CEE, SUST-3114 | # Coordinator, CRTC Dept. of CEE, SUST-3114 |