Ref. no: CRTC/CEE/G20220223/S- 41

SUB-SOIL INVESTIGATION REPORT FOR

PROPOSED ON 04 STORIED RESIDENTIAL BUILDING

AT VILL-KUSHIGHAT, BURHANABAD, SYLHET

DAG # SA-91, KHA # SA-61, BS-3344,3345, J.L # 99, MOUJA-TULTIKOR

CLIENT

ABUL KHAIR & RIMA BEGUM

CONDUCTED BY

CENTER FOR RESEARCH TESTING & CONSULTANCY

DEPARTMENT OF CIVIL & ENVIRONMENTAL ENGINEERING

SHAHJALAL UNIVERSITY OF SCIENCE & TECHNOLOGY, SYLHET

Sample Collected by

THE UNIVERSAL SOIL & ENGINEERING

Moktosor Market (2nd Floor), Shop # 6, Bagbari Point, Sylhet.

Mobile: 01741-217881

##### Introduction

A reasonably accurate conception about the sub-soil parameters of any project site is an essential prerequisite for proper planning and designing the foundation of the structure so that the same after its construction would remain safe and serviceable. A detailed study on the sub-surface elements in this regard would necessary to select proper type of foundation.

Objectives

The purpose of sub-soil investigation program is to obtain the following information

- To classify the formation of soil layers

- To estimate the safe bearing capacities of the foundation at different soil layers

- To suggest the safe and appropriate type of foundations.

Scope of work

Centre for research, testing and consultancy (CRTC), Department of Civil and Environmental Engineering, Shahjalal University of Science & Technology (SUST), Sylhet; execute only the laboratory tests and other computational works with the supplied disturbed and/or undisturbed samples to determine the geotechnical properties of the soil.

Table – 1: Items of the supplied samples

| No | Name | Bore hole no | Depth | Quantities |
| --- | --- | --- | --- | --- |
| 01 | Disturbed sample | 01 | 0-20 ft | 4 |
| 02 | Disturbed sample | 02 | 0-20 ft | 4 |
| 03 | Disturbed sample | 03 | 0-20 ft | 4 |

# Laboratory Classifications

The disturbed soil samples, supplied by the client were thoroughly examined and classified roughly (color and type) and noted in accordance with bore hole (BH) and depth (Please see enclosed Tables).

Laboratory Works & Analysis

In addition to visual examination of the sample, Bearing Capacity of soil samples including skin friction & end bearing were calculated.

Bearing capacity for shallow foundation

The N value gives useful information with regards to consistency of cohesive soil and relative density of cohesion less soil. These relationships are given in the following Tables for cohesive and cohesion less soil, respectively.

# Table 2: Relation of N-value with the Consistency and the Unconfined Compressive Strength of Cohesive Soils (after Bowles 1997)

| N-values | Consistency | Unconfined Compressive Strength (qu) |  |
| --- | --- | --- | --- |
|  |  | tsf | kPa |
| 0-2 | Very soft | 0 to 0.25 | 0 to 25 |
| 3-5 | Soft | 0.25 to 0.50 | 25 to 50 |
| 6-9 | Medium | 0.50 to 1 | 50 to 100 |
| 10-16 | Stiff | 1 to 2 | 100 to 200 |
| 17-30 | Very stiff | 2 to 4 | 200 to 400 |
| >30 | Hard | >4 | >400 |

# Table 3: N and  Relation to Relative Density for Fine Sand (after Bowles 1997)

| N values | Compactness | Relative Density, Dr % | (degree) | Unit Weight (pcf) |
| --- | --- | --- | --- | --- |
| 1 – 2 | Very Loose | 0 – 15 | 26 – 28 | 70 – 100 |
| 3 – 6 | Loose | 15 – 35 | 28 – 30 | 90 – 115 |
| 7 – 15 | Medium | 35 – 65 | 30 – 34 | 110 – 130 |
| 16 – 30 | Dense | 65 – 85 | 33 – 38 | 110 – 140 |
| >30 | Very Dense | >85 | >50 | 130 – 150 |

# Table 4: N and  Relation to Relative Density for Medium Sand (after Bowles 1997)

| N values | Compactness | Relative Density, Dr % | (degree) | Unit Weight (pcf) |
| --- | --- | --- | --- | --- |
| 2 – 3 | Very Loose | 0 – 15 | 27 – 28 | 70 – 100 |
| 4 – 7 | Loose | 15 – 35 | 30 – 32 | 90 – 115 |
| 8 – 20 | Medium | 35 – 65 | 32 – 36 | 110 – 130 |
| 21 – 40 | Dense | 65 – 85 | 36 – 42 | 110 – 140 |

# Table 5: N and  Relation to Relative Density for Coarse Sand (after Bowles 1997)

| N values | Compactness | Relative Density, Dr % | (degree) | Unit Weight (pcf) |
| --- | --- | --- | --- | --- |
| 3 – 6 | Very Loose | 0 – 15 | 28 – 30 | 70 – 100 |
| 5 – 9 | Loose | 15 – 35 | 30 – 34 | 90 – 115 |
| 10 – 25 | Medium | 35 – 65 | 33 – 40 | 110 – 130 |
| 26 – 40 | Dense | 65 – 85 | 40 – 50 | 110 – 140 |
| >40 | Very Dense | >85 | >50 | 130 – 150 |

Bearing capacity for deep foundation

Foundations, preferably piles are considered to transmit heavy load from superstructure to deep and hard strata. As the formation of soil strata consists of cohesive and non-cohesive type, the evaluation criteria for the determination of skin friction and the end bearing capacities of piles also vary. Details of the evaluation are provided in the following sub-headings.

Table 6: Formula Used to Determine Bearing Capacity of Soil

| Shallow Foundation |  |
| --- | --- |
| For Cohesive Soil |  |
| qa=qu+γD3 qa=qu(Common Practice) | Where, qa=Allowable bearing capacity, qu= Unconfined Compressive Strength, γ= Unit Weight of soil, D= Depth of footing |
| For Cohesion less Soil |  |
| qult=30N; qa=qultFS | qult= Ultimate bearing capacity in kPa, N = SPT Number, FS= Factor of Safety |
| Source: Bowles, J. E., "Physical and Geotechnical Properties of Soils", 2nd Edition |  |
| Deep Foundation |  |
| For Cohesive Soil |  |
| fsu=αCu ; qpu=NcCu | = Adhesion factor, fsu= Ultimate skin friction, Cu= Undrained Shear Strength, qpu= Ultimate end bearing of pile, Nc= Bearing capacity factor for deep foundation=9 |
| For Cohesion less Soil |  |
| fsu=N50 tsf; qpu=4N tsf | fsu= Ultimate skin friction, qpu= Ultimate end bearing of pile, N = SPT Number |
| Source: Rajapakse RA (2008), “Geotechnical Engineering Calculations and Rules of Thumb” |  |

Based on the above formula, the important parameters for foundation design have been determined and are given in Table 7, Table 8, Table 9, Table 10 and Table 11 respectively.

Table 7: The allowable bearing capacity for shallow foundation in Tsf (FS=2.5)

| Bore Hole No. | Depth | Design N | Clay |  |  |  |  |  | Sand |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Continuous |  |  | Square(Isolated) |  |  |  |  |
|  | (ft) | - | D/B=0.25 | D/B=0.5 | D/B=1 | D/B=0.25 | D/B=0.5 | D/B=1 |  |  |
| BH01 | 2.5-5.0 | 24 | 2.738 | 2.879 | 3.139 | 3.233 | 3.493 | 3.800 | 2.950 |  |
|  | 5.0-10 | 34 | 3.956 | 4.161 | 4.536 | 4.672 | 5.047 | 5.491 | 4.263 |  |
| BH02 | 2.5-5.0 | 27 | 3.132 | 3.294 | 3.591 | 3.699 | 3.996 | 4.347 | 3.375 |  |
|  | 5.0-10 | 39 | 4.528 | 4.762 | 5.192 | 5.348 | 5.777 | 6.285 | 4.879 |  |
| BH03 | 2.5-5.0 | 25 | 2.877 | 3.026 | 3.298 | 3.398 | 3.670 | 3.993 | 3.100 |  |
|  | 5.0-10 | 36 | 4.136 | 4.350 | 4.742 | 4.885 | 5.277 | 5.740 | 4.457 |  |

Table 8: The allowable skin friction for Precast driven piles in Tsf (FS=2.5)

| Depth | Bore Hole |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ft | BH01 | BH02 | BH03 | BH04 | BH05 | BH06 | BH07 | BH08 | BH09 | BH10 |
| 5 | 0.226 | 0.240 | 0.241 | - | - | - | - | - | - | - |
| 10 | 0.281 | 0.375 | 0.348 | - | - | - | - | - | - | - |
| 15 | 0.401 | 0.415 | 0.361 | - | - | - | - | - | - | - |
| 20 | 0.669 | 0.762 | 0.709 | - | - | - | - | - | - | - |

Table 9: The allowable end bearing for Precast driven piles in Tsf (FS=2.5)

| Depth | Bore Hole |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ft | BH01 | BH02 | BH03 | BH04 | BH05 | BH06 | BH07 | BH08 | BH09 | BH10 |
| 5 | 3.600 | 3.825 | 4.050 | - | - | - | - | - | - | - |
| 10 | 4.725 | 6.300 | 5.850 | - | - | - | - | - | - | - |
| 15 | 6.750 | 6.975 | 6.075 | - | - | - | - | - | - | - |
| 20 | 11.250 | 12.825 | 11.925 | - | - | - | - | - | - | - |

Table 10: The allowable skin friction for Bored piles in Tsf (FS=2.5)

| Depth | Bore Hole |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ft | BH01 | BH02 | BH03 | BH04 | BH05 | BH06 | BH07 | BH08 | BH09 | BH10 |
| 5 | 0.147 | 0.156 | 0.156 | - | - | - | - | - | - | - |
| 10 | 0.183 | 0.243 | 0.226 | - | - | - | - | - | - | - |
| 15 | 0.261 | 0.270 | 0.235 | - | - | - | - | - | - | - |
| 20 | 0.435 | 0.496 | 0.461 | - | - | - | - | - | - | - |

Table 11: The allowable end bearing for Bored piles in Tsf (FS=3.0)

| Depth | Bore Hole |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ft | BH01 | BH02 | BH03 | BH04 | BH05 | BH06 | BH07 | BH08 | BH09 | BH10 |
| 5 | 1.620 | 1.721 | 1.823 | - | - | - | - | - | - | - |
| 10 | 2.126 | 2.835 | 2.633 | - | - | - | - | - | - | - |
| 15 | 3.038 | 3.139 | 2.734 | - | - | - | - | - | - | - |
| 20 | 5.063 | 5.771 | 5.366 | - | - | - | - | - | - | - |

\

CONCLUSION AND RECOMMENDATION

On the basis of analysis and information provided by the owner following recommendations are suggested for the proposed four storied building.

Soil profile scenario

Overall soil information of the investigated site is quite regular in between the boreholes and vertical consistency in the soil formation at different layers was observed. Nearly hard clay soil with stiffness scenario has been observed among the boreholes. For borehole 1 to 3 at top surface, there is layer of brown stiff clay in most of the site.  There is a dense and hard clay layer below 5ft from ground level in most of the site. There is hard clay layer below 10ft in the site.

Foundation options

In this situation, the foundation should be selected considering both the dimension and design load for the proposed building. Since stiff clay layer is found at 5ft, isolated foundation can be adopted at 7ft for proposed four storied building. The bearing capacity for shallow foundation which is given in table 7 is based on existing soil conditions. However, client needs to reassess the improved bearing capacity of the prepared ground after implementing soil improvement technique in the top layer as mentioned above.

Safety provisions

Since the proposed site is composed of alternate layers of soft cohesive and granular soil, it is reasonably vulnerable to differential settlement. Therefore, it is strongly recommended to check the settlement of the site considering building load while designing either shallow or deep foundation. Obviously pile load test covering the entire project area must be carried out for confirming the design parameters of the service pile (if pile foundation is considered). Moreover, the earthquake vulnerability of the project area as well as the quality management of the construction work including workmanship should be taken into account for the safe design of shallow or deep foundation.

Attachments

The layout of the bore holes of the investigated site and the bore-log profiles with SPT values is shown in the Appendix. Client performed no special laboratory test for the proposed site.

Special notes

These suggestions are absolutely tentative and selection of type, depth and dimensions of foundation would be decided by the Consultant or Design Engineer. It is also to be noted that the above recommendation is restricted only to the existing soil condition as client provided.

| Test Assisted By | Report Prepared By | Countersigned By |
| --- | --- | --- |
| A.H.M. Humayun Kabir | Dr. Md. Jahir Bin Alam | # Prof. Dr. Imran Kabir |
| Senior Technical Officer Dept. of CEE, SUST-3114 | Professor Dept. of CEE, SUST-3114 | # Coordinator Dept. of CEE, SUST, Sylhet-3114 |